## Instructions
Radiant Panel Emissions Model and Sizing Tool
If you need help sizing panels or would like to discuss your requirements, please call us on 01792 892211 or email sales@solray.co.uk
Thank you for downloading and using our radiant panel emissions model and sizing tool. We hope you find it helpful.
This spreadsheet contains two tabs in addition to this one:
1 | Panel Emissions
This tab models the radiant emissions of our panels for various mean water temperatures and ambient temperatures giving outputs in watts per square metre or watts per linear metre for a given width. By completing the yellow shaded cells, you can personalise the results to take account of the faceplate material, heating medium, panel width, the panel position and orientation, and any wall gap.
2 | Panel Sizer Tool
This tool enables you to calculate the length of panels you require based on room specifications and your personalised panel outputs

## Panel Emissions
Solray Ceiling Panel Emissions per area (W/m²)
Ver 7.2
If you need help sizing panels or would like to discuss your requirements, please call us on 01792 892211 or email sales@solray.co.uk
The table and graph below calculate radiant panel emissions based on your specifications. Yellow shaded cells require you to input data whilst grey shaded cells calculate themselves based on your inputs. See below for further instructions.
Project Name | [8 empty] | Your Ref | Date
Assumptions |  | Faceplate | Painted Aluminium
(See notes below) |  | Medium | Hot Water
(a) | 600 | mm Panel width
(b) | 2.7 | m Mounting height
| 0% | derating for high mounting positions
(c) | 90 | ° to Vertical mounting angle
(d) | 0 | mm deep gap behind a wall panel
| 0% | increase in convection |  |  | 0%
0%
Display emissions: | by heated panel area
Mean Water | Emissions per area (W/m²)
Temperature | Ambient Temperature /°C
/°C | 16 | 17 | 18 | 19 | 20 | 21 | 25 | 22
60 | 360 | 350 | 345 | 335 | 330 | 320 | 290
65 | 410 | 400 | 395 | 385 | 380 | 370 | 340
70 | 460 | 455 | 445 | 440 | 430 | 420 | 390
75 | 515 | 510 | 500 | 490 | 485 | 475 | 445
76.67 | 535 | 525 | 520 | 510 | 500 | 495 | 460
80 | 570 | 565 | 555 | 550 | 540 | 530 | 500
85 | 630 | 620 | 615 | 605 | 595 | 590 | 555
90 | 690 | 680 | 675 | 665 | 655 | 650 | 615
95 | 750 | 740 | 735 | 725 | 715 | 710 | 675
100 | 815 | 805 | 795 | 790 | 780 | 770 | 740
105 | 880 | 870 | 860 | 855 | 845 | 835 | 805
110 | 945 | 935 | 930 | 920 | 910 | 905 | 870
115 | 1015 | 1005 | 1000 | 990 | 980 | 970 | 940
Additional notes and instructions for use
(a) | Width of Solray panel: default is 600mm
(b) | Mounting height of the panel above the floor in metres
(c) | Angles are 90°: Ceiling, 0°: Wall, -90°: Floor, 0°-90°: Angled at another angle
(d) | Gap behind, and around edges of, a wall panel in mm
(f) | You can adjust the ranges for mean water temperature and ambient temperature - just type new numbers into the yellow shaded cells in the table above.
(g) | You can extend the axes of the graph by removing the minimum value (left click on the axis to select it, then right click to bring up menu , then left click on 'format axis')
(h) | Outputs do not include cold areas within panels - for example access plates for plasterboard.
0
Ambient Temperature /°C

## Panel Sizer Tool
Solray Panel Sizing Tool
If you need help sizing panels or would like to discuss your requirements, please call us on 01792 892211 or email sales@solray.co.uk
This calculator is designed to work out the length of Solray panels required given the parameters you enter. Yellow cells require you to input information (some have defaults which can be over-written), grey cells calculate themselves. See notes below table for additional guidance.
|  | Project Name | [9 empty] | Your Ref |  |  |  | Date:
|  | Project Mean Water Temp* |  | °C
[13 empty] | Solray Tridents or FH Strips |  |  | Solray DM Perimeters
Line No | Room Ref No | Room Name | Room Resultant Temperature /°C | Required Heat Load /W | Room Length /mm | Room Width /mm | Load per floor area (W/m²) | Mounting Height Angle /m /° |  | Solray Panel Emission (W/m²) | Heated Area Required/m² | Guide max width for comfort /mm | Trident or FH Width /mm | Number of Tridents or FHs | Each Trident or FH Length Required /mm | DM Arrangement | Total DM Length /mm | DM Width /mm | Flow Rate (kg/s) | Pressure Drops /Pa | Comments
1 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
2 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
3 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
4 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
5 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
6 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
7 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
8 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
9 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
10 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
11 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
12 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
13 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
14 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
15 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
16 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
17 | [7 empty] | 2.7 | 90 |  |  |  | 600 |  |  |  |  | 0 | TBC | TBC
[13 empty] | 0 | Trident connection pairs |  | 0 | DM Connection pairs
This is the number of connection pairs required for either option, for calculating valves, etc
Additional guidance
* | Enter the mean water temperature, which should feature in the table on the Emissions tab | [10 empty] | Yes
Notes for each column in table above | [8 empty] | Extras required in quotation: |  |  | No
C | Enter a reference number for your room | [7 empty] | Installation
D | Enter the name of your room | [7 empty] | RAL colour (9010 is standard)
E | Enter the room target resultant temperature | [7 empty] | Drain cocks at all low points
F | Enter the heat load required for your room in watts | [7 empty] | Valves
G | Enter the room length (the preferred position for the Solray Panel, often the window wall) | [7 empty] | Flexibles
H | Enter the room width (an internal wall) | [7 empty] | Black bulb sensors
I | This is the load per unit floor area, to check no large error in load or lengths | [7 empty] | Premium encapsulated insulation
J | Accept the mounting height, copied from the Panel Emissions tab, or over-write with specific value for the room
K | Accept the mounting angle, copied from the Panel Emissions tab, or over-write with specific value for the room
L | Accept the Solray Panel Emission in watts per m², or over-write with specific value for the room (will require manual entry for special parameters)
M | Automatically calculated heating area of Solray panels required to provide the output
N | Our recommended maximum width to avoid oppressiveness for most people, for the temperatures and mounting height
Calculation follows for Solray Tridents, SFH Strips and Solray DM Perimeters
For help on which (or another) might be the best type applicable for the project, please call us
O | Accept the Solray Trident/FH width, or over-write with specific value for the room
P | Accept the calculated number of Solray Tridents/FHs, or over-write with another number
Q | Automatically calculated length of Solray Tridents/FH required
R | Recommended arrangement for a Solray DM Perimeter
S | Solray DM Perimeter Length for arrangement
T | Solray DM Perimeter Width for arrangement
U | For a schedule with flow rates and pressure drops, and a quotation, please send this schedule to sales@solray.co.uk
V | For a schedule with flow rates and pressure drops, and a quotation, please send this schedule to sales@solray.co.uk
W | Any comments?

## Calculations (hidden)
Mean Water | Emission (W/m²)
Temperature | Ambient Temperature /°C
/°C | 16 | 17 | 18 | 19 | 20 | 21 | 25
60 | 358.8109 | 351.0336 | 343.2306 | 335.4019 | 327.5477 | 319.6679 | 287.8967
65 | 409.3617 | 401.509 | 393.6289 | 385.7212 | 377.7861 | 369.8236 | 337.6997
70 | 461.6928 | 453.7734 | 445.8251 | 437.8478 | 429.8415 | 421.8061 | 389.3736
75 | 515.8031 | 507.8244 | 499.8156 | 491.7766 | 483.7073 | 475.6076 | 442.903
76.67 | 534.273 | 526.276 | 518.2485 | 510.1905 | 502.1017 | 493.9822 | 461.194
80 | 571.6973 | 563.6659 | 555.6033 | 547.5095 | 539.3842 | 531.2273 | 498.2821
85 | 629.3849 | 621.3065 | 613.1961 | 605.0534 | 596.8783 | 588.6707 | 555.512
90 | 688.879 | 680.7589 | 672.6058 | 664.4197 | 656.2004 | 647.9477 | 614.5994
95 | 750.1961 | 742.0388 | 733.8479 | 725.6233 | 717.3647 | 709.0719 | 675.5555
100 | 813.3552 | 805.165 | 796.9407 | 788.6819 | 780.3885 | 772.0603 | 738.395
105 | 878.3776 | 870.1585 | 861.9047 | 853.6158 | 845.2918 | 836.9323 | 803.1359
110 | 945.2868 | 937.0425 | 928.7628 | 920.4477 | 912.0968 | 903.71 | 869.7985
115 | 1014.108 | 1005.8418 | 997.5398 | 989.2019 | 980.8278 | 972.4172 | 938.4057
| Medium List | Material list | Emission Basis |  |  |  | Amendments
| 1 | 2 | 1 |  |  |  | 1.01 | 2000-08-01 | 6th column added
| Hot Water | Painted Steel | 1 | by heated panel area |  |  | 1.02 | 2000-08-02 | Axes labels corrected
| Steam | Painted Aluminium | 2 | by heated length of a 600mm wide panel |  |  | 1.03 | 2001-06-16 | Derating corrected
| Electric | Stainless Steel |  |  |  |  | 1.04 | 2014-02-19 | Axes adjustable
| Double Tube Hot Water | Anodised Aluminium | [6 empty] | Perforated added
|  | Plastic-coated steel |  |  |  |  | 6 | 2017-07-06 | 7th column added, format changed for user experience, linear metre tab added, panel sizer moved to separate tab
|  | Perforated Steel |  |  |  |  | 7 | 2017-07-09 | Area tab changed to include linear metre; no macros
Perforated Aluminium
| Graph Axes Headings | Emissions per area (W/m²)
Mean Water Temperature /°C
Ambient Temperature /°C
Emissions per area (W/m²)